## ROOM_SPEC
検索キー | 建物用途コード | 室分類コード | 照明発熱参照値 | 人体発熱参照値 | 機器発熱参照値 | 外気導入量 | パターン1空調開始時刻1 | パターン1空調終了時刻1 | パターン1空調開始時刻2 | パターン1空調終了時刻2 | パターン2空調開始時刻1 | パターン2空調終了時刻1 | パターン2空調開始時刻2 | パターン2空調終了時刻2 | 年間空調時間 | 年間照明点灯時間 | 基準設定照度 | 基準照明消費電力 | 年間換気時間 | 基準設定換気風量 | 基準設定全圧損失 | 基準設定湯使用量 | 基準設定湯使用量 | 年間給湯 日数
ID | Building type | Room type | Ref. value of internal heat gain(lighting) [W/m2] | Ref. value of internal heat gain(metabolism) [person/m2] | Ref. value of internal heat gain(OA equipment) [W/m2] | Fresh air intake [m3/m2/h] | <Week day 1> The time to start air coditioning | <Week day 1> The time to stop air coditioning | <Week day 2> The time to start air coditioning | <Week day 2> The time to stop air coditioning | <Saturday 1> The time to start air coditioning | <Saturday 1> The time to stop air coditioning | <Saturday 2> The time to start air coditioning | <Saturday 2> The time to stop air coditioning | Operation time for air conditioning [hours/year] | Operation time for lighting [hours/year] | Illuminance level [lx] | Ref. power consumption for lighting [W/m2] | Operation time for ventilation except air conditioning [hours/year] | Ref. air volume for ventilation [m3/m2/h] | Ref. pressure loss for ventilation ducts [Pa] | Ref. hot-water usage | Unit of ref. hot-water usage | Operation days for hot-water supply [days/year]
O-1 | Office | OfficeRoom | 12 | 0.1 | 12 | 5 | 7 | 21 |  |  |  | 0 |  |  | 3374 | 3133 | 750 | 16.3 | 0 | 0 | 0 | 3.8 | [L/person/day] | 241
O-2 | Office | ComputerRoom | 12 | 0.1 | 30 | 5 | 7 | 21 |  |  |  | 0 |  |  | 3374 | 3133 | 750 | 16.3 | 0 | 0 | 0 | 3.8 | [L/person/day] | 241
O-3 | Office | MeetingRoom | 10 | 0.25 | 2 | 12 | 8 | 18 |  |  |  | 0 |  |  | 2410 | 2169 | 500 | 10.9 | 0 | 0 | 0 | 3.8 | [L/person/day] | 241
O-4 | Office | TeaRoom | 10 | 0.25 | 2 | 12 | 8 | 18 |  |  |  | 0 |  |  | 2410 | 2169 | 300 | 12 | 0 | 0 | 0 | 32 | [L/m2/day] | 241
O-5 | Office | Canteen | 30 | 0.5 | 0 | 15 | 11 | 14 |  |  |  | 0 |  |  | 723 | 723 | 500 | 20 | 0 | 0 | 0 | 48 | [L/m2/day] | 241
O-6 | Office | CentralMonitoringRoom | 20 | 0.15 | 30 | 4 | 0 | 24 |  |  | 0 | 24 |  |  | 8760 | 8760 | 500 | 13.7 | 0 | 0 | 0 | 3.8 | [L/person/day] | 365
O-7 | Office | LockerRoom | 15 | 0.3 | 0 | 4 | 7 | 21 |  |  |  | 0 |  |  | 3374 | 3133 | 300 | 6.6 | 3133 | 13.5 | 300 | 62 | [L/person/day] | 241
O-8 | Office | Corridor | 15 | 0.03 | 0 | 2.5 | 8 | 21 |  |  |  | 0 |  |  | 3133 | 3133 | 200 | 8 | 0 | 0 | 0 | 0 | - | 0
O-9 | Office | Lobby | 15 | 0.03 | 0 | 2.5 | 8 | 21 |  |  |  | 0 |  |  | 3133 | 3133 | 500 | 17.9 | 0 | 0 | 0 | 3.8 | [L/person/day] | 241
O-10 | Office | Toilet | 15 | 0.03 | 0 | 2.5 | 8 | 21 |  |  |  | 0 |  |  | 3133 | 3133 | 300 | 12 | 3133 | 40.5 | 300 | 0 | - | 0
O-11 | Office | SmokingRoom | 15 | 0.03 | 0 | 2.5 | 8 | 21 |  |  |  | 0 |  |  | 3133 | 3133 | 300 | 6.6 | 3133 | 81 | 300 | 0 | - | 0
O-12 | Office | Kitchen | [12 empty] | 0 | 2000 | 750 | 16.5 | 2000 | 135 | 600 | 0 | - | 0
O-13 | Office | IndoorParking | [12 empty] | 0 | 3500 | 150 | 3.6 | 3500 | 30 | 600 | 0 | - | 0
O-14 | Office | MechanicalRoom | [12 empty] | 0 | 200 | 200 | 4.9 | 8760 | 13.5 | 300 | 0 | - | 0
O-15 | Office | ElectricalRoom | [12 empty] | 0 | 200 | 200 | 4.9 | 8760 | 27 | 300 | 0 | - | 0
O-16 | Office | Kitchenette | [12 empty] | 0 | 1000 | 300 | 6.6 | 2000 | 13.5 | 300 | 0 | - | 0
O-17 | Office | StorageRoom | [12 empty] | 0 | 1000 | 300 | 7.2 | 2000 | 13.5 | 300 | 0 | - | 0
O-18 | Office | CopyRoom | [12 empty] | 0 | 1000 | 500 | 10.9 | 2000 | 27 | 300 | 0 | - | 0
O-19 | Office | GarbageStorage | [12 empty] | 0 | 1000 | 150 | 3.6 | 2000 | 40.5 | 300 | 0 | - | 0
H-1 | Hotel | GuestRoom | 15 | 0.07 | 4 | 4 | 0 | 10 | 19 | 24 | 0 | 10 | 19 | 24 | 5475 | 2920 | 300 | 10.8 | 0 | 0 | 0 | 165 | [L/person/day] | 365
H-2 | Hotel | BathroomInGuestRoom | 15 | 0.07 | 4 | 4 | 0 | 10 | 19 | 24 | 0 | 10 | 19 | 24 | 5475 | 2920 | 300 | 12 | 5475 | 21.6 | 300 | 165 | [L/person/day] | 365
H-3 | Hotel | FrontDesk_AllDay | 20 | 0.1 | 0 | 2.5 | 0 | 24 |  |  | 0 | 24 |  |  | 8760 | 8760 | 500 | 20 | 0 | 0 | 0 | 0 | - | 0
H-4 | Hotel | OfficeRoom_AllDay | 20 | 0.2 | 10 | 5 | 0 | 24 |  |  | 0 | 24 |  |  | 8760 | 8760 | 750 | 16.3 | 0 | 0 | 0 | 3.8 | [L/person/day] | 365
H-5 | Hotel | Corridor_AllDay | 10 | 0.05 | 0 | 2.5 | 0 | 24 |  |  | 0 | 24 |  |  | 8760 | 8760 | 150 | 6 | 0 | 0 | 0 | 0 | - | 0
H-6 | Hotel | Lobby_AllDay | 20 | 0.1 | 0 | 2.5 | 0 | 24 |  |  | 0 | 24 |  |  | 8760 | 8760 | 300 | 12 | 0 | 0 | 0 | 3.8 | [L/person/day] | 365
H-7 | Hotel | Toilet_AllDay | 20 | 0.1 | 0 | 2.5 | 0 | 24 |  |  | 0 | 24 |  |  | 8760 | 8760 | 300 | 12 | 8760 | 40.5 | 300 | 0 | - | 0
H-8 | Hotel | SmokingRoom_AllDay | 20 | 0.1 | 0 | 2.5 | 0 | 24 |  |  | 0 | 24 |  |  | 8760 | 8760 | 300 | 6.6 | 8760 | 81 | 300 | 0 | - | 0
H-9 | Hotel | BanquetHall | 100 | 0.7 | 12 | 20 | 9 | 21 |  |  | 9 | 21 |  |  | 4380 | 4380 | 750 | 30 | 0 | 0 | 0 | 3.8 | [L/person/day] | 365
H-10 | Hotel | ConferenceRoom | 50 | 0.7 | 0 | 20 | 9 | 21 |  |  | 9 | 21 |  |  | 4380 | 4380 | 750 | 30 | 0 | 0 | 0 | 3.8 | [L/person/day] | 365
H-11 | Hotel | WeddingHall | 30 | 0.3 | 0 | 7.5 | 8 | 20 |  |  | 8 | 20 |  |  | 4380 | 4380 | 750 | 30 | 0 | 0 | 0 | 3.8 | [L/person/day] | 365
H-12 | Hotel | Restaurant | 20 | 0.5 | 10 | 12.5 | 6 | 21 |  |  | 6 | 21 |  |  | 5475 | 4745 | 300 | 12 | 0 | 0 | 0 | 48 | [L/m2/day] | 365
H-13 | Hotel | Lounge | 20 | 0.2 | 0 | 5 | 7 | 21 |  |  | 7 | 21 |  |  | 5110 | 5110 | 300 | 12 | 0 | 0 | 0 | 3.8 | [L/person/day] | 365
H-14 | Hotel | Bar | 10 | 0.2 | 0 | 5 | 18 | 24 |  |  | 18 | 24 |  |  | 2190 | 2190 | 150 | 6 | 0 | 0 | 0 | 3.8 | [L/person/day] | 365
H-15 | Hotel | Shop | 30 | 0.1 | 30 | 10 | 9 | 19 |  |  | 9 | 19 |  |  | 3650 | 3650 | 500 | 17.9 | 0 | 0 | 0 | 3.8 | [L/person/day] | 365
H-16 | Hotel | Canteen | 20 | 0.5 | 0 | 12.5 | 6 | 21 |  |  | 6 | 21 |  |  | 5475 | 5110 | 500 | 20 | 0 | 0 | 0 | 48 | [L/m2/day] | 365
H-17 | Hotel | LockerRoom | 15 | 0.1 | 0 | 5 | 0 | 24 |  |  | 0 | 24 |  |  | 8760 | 8760 | 300 | 6.6 | 8760 | 13.5 | 300 | 62 | [L/person/day] | 365
H-18 | Hotel | FrontDesk_Daytime | 35 | 0.2 | 0 | 7.5 | 8 | 21 |  |  | 8 | 21 |  |  | 4745 | 4745 | 500 | 20 | 0 | 0 | 0 | 0 | - | 0
H-19 | Hotel | OfficeRoom_Daytime | 20 | 0.2 | 10 | 5 | 7 | 22 |  |  | 7 | 22 |  |  | 5475 | 5475 | 750 | 16.3 | 0 | 0 | 0 | 3.8 | [L/person/day] | 365
H-20 | Hotel | Corridor_Daytime | 10 | 0.1 | 0 | 5 | 8 | 21 |  |  | 8 | 21 |  |  | 4745 | 4745 | 150 | 6 | 0 | 0 | 0 | 0 | - | 0
H-21 | Hotel | Lobby_Daytime | 35 | 0.2 | 0 | 7.5 | 8 | 21 |  |  | 8 | 21 |  |  | 4745 | 4745 | 300 | 12 | 0 | 0 | 0 | 3.8 | [L/person/day] | 365
H-22 | Hotel | Toilet_Daytime | 35 | 0.2 | 0 | 7.5 | 8 | 21 |  |  | 8 | 21 |  |  | 4745 | 4745 | 300 | 12 | 4745 | 40.5 | 300 | 0 | - | 0
H-23 | Hotel | SmokingRoom_Daytime | 35 | 0.2 | 0 | 7.5 | 8 | 21 |  |  | 8 | 21 |  |  | 4745 | 4745 | 300 | 6.6 | 4745 | 81 | 300 | 0 | - | 0
H-24 | Hotel | Kitchen | [12 empty] | 0 | 3200 | 750 | 16.5 | 3200 | 135 | 600 | 0 | - | 0
H-25 | Hotel | IndoorParking | [12 empty] | 0 | 8760 | 150 | 3.6 | 8760 | 30 | 600 | 0 | - | 0
H-26 | Hotel | MechanicalRoom | [12 empty] | 0 | 320 | 200 | 4.9 | 8760 | 13.5 | 300 | 0 | - | 0
H-27 | Hotel | ElectricalRoom | [12 empty] | 0 | 320 | 200 | 4.9 | 8760 | 27 | 300 | 0 | - | 0
H-28 | Hotel | Kitchenette | [12 empty] | 0 | 1600 | 300 | 6.6 | 3200 | 13.5 | 300 | 0 | - | 0
H-29 | Hotel | StorageRoom | [12 empty] | 0 | 1600 | 300 | 7.2 | 3200 | 13.5 | 300 | 0 | - | 0
H-30 | Hotel | CopyRoom | [12 empty] | 0 | 1600 | 500 | 10.9 | 3200 | 27 | 300 | 0 | - | 0
H-31 | Hotel | GarbageStorage | [12 empty] | 0 | 1600 | 150 | 3.6 | 3200 | 40.5 | 300 | 0 | - | 0
D-1 | Hospital | Ward | 12 | 0.08 | 3 | 4 | 0 | 24 |  |  | 0 | 24 |  |  | 8760 | 5110 | 300 | 10.3 | 0 | 0 | 0 | 284.2 | [L/床日] | 365
D-2 | Hospital | Bathroom | 12 | 0.08 | 3 | 4 | 0 | 24 |  |  | 0 | 24 |  |  | 8760 | 5110 | 300 | 12 | 8760 | 21.6 | 300 | 284.2 | [L/床日] | 365
D-3 | Hospital | StaffStation | 12 | 0.08 | 3 | 4 | 0 | 24 |  |  | 0 | 24 |  |  | 8760 | 5110 | 750 | 16.3 | 0 | 0 | 0 | 3.3 | [L/m2/day] | 365
D-4 | Hospital | Corridor_AllDay | 20 | 0.05 | 0 | 5 | 0 | 24 |  |  | 0 | 24 |  |  | 8760 | 8760 | 300 | 6.6 | 0 | 0 | 0 | 0 | - | 0
D-5 | Hospital | Lobby_AllDay | 20 | 0.05 | 0 | 5 | 0 | 24 |  |  | 0 | 24 |  |  | 8760 | 8760 | 300 | 12 | 0 | 0 | 0 | 3.8 | [L/person/day] | 365
D-6 | Hospital | Toilet_AllDay | 20 | 0.05 | 0 | 5 | 0 | 24 |  |  | 0 | 24 |  |  | 8760 | 8760 | 300 | 12 | 8760 | 40.5 | 300 | 0 | - | 0
D-7 | Hospital | SmokingRoom_AllDay | 20 | 0.05 | 0 | 5 | 0 | 24 |  |  | 0 | 24 |  |  | 8760 | 8760 | 300 | 7.4 | 8760 | 81 | 300 | 0 | - | 0
D-8 | Hospital | ConsultingRoom | 20 | 0.2 | 15 | 5 | 8 | 18 |  |  | 8 | 16 |  |  | 2818 | 2818 | 750 | 16.3 | 0 | 0 | 0 | 3.3 | [L/m2/day] | 292
D-9 | Hospital | WaitingLounge | 20 | 0.2 | 15 | 5 | 8 | 18 |  |  | 8 | 16 |  |  | 2818 | 2818 | 500 | 11 | 0 | 0 | 0 | 3.3 | [L/m2/day] | 292
D-10 | Hospital | OperatingRoom | 20 | 0.1 | 30 | 10 | 8 | 18 |  |  | 8 | 18 |  |  | 2920 | 2920 | 1500 | 32.6 | 0 | 0 | 0 | 6.3 | [L/m2/day] | 292
D-11 | Hospital | ExaminingRoom | 20 | 0.1 | 30 | 10 | 8 | 18 |  |  | 8 | 18 |  |  | 2920 | 2920 | 750 | 16.3 | 0 | 0 | 0 | 6.3 | [L/m2/day] | 292
D-12 | Hospital | IntensiveCareUnit | 20 | 0.1 | 30 | 4 | 0 | 24 |  |  | 0 | 24 |  |  | 8760 | 8760 | 750 | 16.3 | 0 | 0 | 0 | 6.3 | [L/m2/day] | 365
D-13 | Hospital | DissectingRoom | 20 | 0.2 | 15 | 5 | 8 | 18 |  |  | 8 | 18 |  |  | 2920 | 2628 | 75 | 1.7 | 0 | 0 | 0 | 3.8 | [L/person/day] | 292
D-14 | Hospital | Restaurant | 20 | 0.1 | 10 | 4 | 7 | 19 |  |  | 7 | 19 |  |  | 4380 | 4380 | 500 | 12.2 | 0 | 0 | 0 | 48 | [L/m2/day] | 365
D-15 | Hospital | OfficeRoom | 20 | 0.2 | 15 | 5 | 8 | 18 |  |  | 8 | 18 |  |  | 2920 | 2628 | 750 | 16.3 | 0 | 0 | 0 | 3.8 | [L/person/day] | 292
D-16 | Hospital | LockerRoom | 15 | 0.1 | 0 | 5 | 8 | 18 |  |  | 8 | 18 |  |  | 2920 | 2628 | 300 | 6.6 | 2920 | 13.5 | 300 | 62 | [L/person/day] | 292
D-17 | Hospital | Corridor_Daytime | 20 | 0.05 | 0 | 5 | 8 | 18 |  |  | 8 | 18 |  |  | 2920 | 2920 | 300 | 6.6 | 0 | 0 | 0 | 0 | - | 0
D-18 | Hospital | Lobby_Daytime | 20 | 0.05 | 0 | 5 | 8 | 18 |  |  | 8 | 18 |  |  | 2920 | 2920 | 300 | 12 | 0 | 0 | 0 | 3.8 | [L/person/day] | 292
D-19 | Hospital | Toilet_Daytime | 20 | 0.05 | 0 | 5 | 8 | 18 |  |  | 8 | 18 |  |  | 2920 | 2920 | 300 | 12 | 2920 | 40.5 | 300 | 0 | - | 0
D-20 | Hospital | SmokingRoom_Daytime | 20 | 0.05 | 0 | 5 | 8 | 18 |  |  | 8 | 18 |  |  | 2920 | 2920 | 300 | 6.6 | 2920 | 81 | 300 | 0 | - | 0
D-21 | Hospital | Kitchen | [12 empty] | 0 | 5500 | 750 | 16.5 | 5500 | 135 | 600 | 0 | - | 0
D-22 | Hospital | IndoorParking | [12 empty] | 0 | 8760 | 150 | 3.6 | 8760 | 30 | 600 | 0 | - | 0
D-23 | Hospital | MechanicalRoom | [12 empty] | 0 | 550 | 200 | 4.9 | 8760 | 13.5 | 300 | 0 | - | 0
D-24 | Hospital | ElectricalRoom | [12 empty] | 0 | 550 | 200 | 4.9 | 8760 | 27 | 300 | 0 | - | 0
D-25 | Hospital | Kitchenette | [12 empty] | 0 | 2800 | 300 | 6.6 | 5500 | 13.5 | 300 | 0 | - | 0
D-26 | Hospital | StorageRoom | [12 empty] | 0 | 2800 | 300 | 7.2 | 5500 | 13.5 | 300 | 0 | - | 0
D-27 | Hospital | CopyRoom | [12 empty] | 0 | 2800 | 500 | 10.9 | 5500 | 27 | 300 | 0 | - | 0
D-28 | Hospital | GarbageStorage | [12 empty] | 0 | 2800 | 150 | 3.6 | 5500 | 40.5 | 300 | 0 | - | 0
S-1 | Store | LargeScaleRetailStore | 30 | 0.2 | 40 | 7.5 | 9 | 22 |  |  | 9 | 22 |  |  | 4745 | 4745 | 750 | 20.1 | 0 | 0 | 0 | 3.8 | [L/person/day] | 365
S-2 | Store | SpecializedStore | 30 | 0.2 | 40 | 7.5 | 9 | 22 |  |  | 9 | 22 |  |  | 4745 | 4745 | 500 | 17.9 | 0 | 0 | 0 | 3.8 | [L/person/day] | 365
S-3 | Store | Supermarket | 30 | 0.2 | 40 | 7.5 | 9 | 22 |  |  | 9 | 22 |  |  | 4745 | 4745 | 750 | 16.5 | 0 | 0 | 0 | 3.8 | [L/person/day] | 365
S-4 | Store | Backyard | 15 | 0.1 | 5 | 5 | 10 | 18 |  |  | 10 | 18 |  |  | 2920 | 2920 | 200 | 4.4 | 0 | 0 | 0 | 3.8 | [L/person/day] | 365
S-5 | Store | OfficeRoom | 20 | 0.2 | 15 | 5 | 9 | 22 |  |  | 9 | 22 |  |  | 4745 | 4745 | 750 | 16.3 | 0 | 0 | 0 | 3.8 | [L/person/day] | 365
S-6 | Store | LockerRoom | 15 | 0.1 | 0 | 5 | 9 | 22 |  |  | 9 | 22 |  |  | 4745 | 4745 | 300 | 6.6 | 4745 | 13.5 | 300 | 62 | [L/person/day] | 365
S-7 | Store | Lobby | 30 | 0.1 | 0 | 2.5 | 9 | 22 |  |  | 9 | 22 |  |  | 4745 | 4745 | 750 | 26.9 | 0 | 0 | 0 | 3.8 | [L/person/day] | 365
S-8 | Store | Toilet | 30 | 0.1 | 0 | 2.5 | 9 | 22 |  |  | 9 | 22 |  |  | 4745 | 4745 | 300 | 12 | 4745 | 40.5 | 300 | 0 | - | 0
S-9 | Store | SmokingRoom | 30 | 0.1 | 0 | 2.5 | 9 | 22 |  |  | 9 | 22 |  |  | 4745 | 4745 | 300 | 6.6 | 4745 | 81 | 300 | 0 | - | 0
S-10 | Store | Kitchen | [12 empty] | 0 | 3400 | 750 | 16.5 | 3400 | 135 | 600 | 0 | - | 0
S-11 | Store | IndoorParking | [12 empty] | 0 | 5500 | 150 | 3.6 | 5500 | 30 | 600 | 0 | - | 0
S-12 | Store | MechanicalRoom | [12 empty] | 0 | 340 | 200 | 4.9 | 8760 | 13.5 | 300 | 0 | - | 0
S-13 | Store | ElectricalRoom | [12 empty] | 0 | 340 | 200 | 4.9 | 8760 | 27 | 300 | 0 | - | 0
S-14 | Store | Kitchenette | [12 empty] | 0 | 1700 | 300 | 6.6 | 3400 | 13.5 | 300 | 0 | - | 0
S-15 | Store | StorageRoom | [12 empty] | 0 | 1700 | 300 | 7.2 | 3400 | 13.5 | 300 | 0 | - | 0
S-16 | Store | CopyRoom | [12 empty] | 0 | 1700 | 500 | 10.9 | 3400 | 27 | 300 | 0 | - | 0
S-17 | Store | GarbageStorage | [12 empty] | 0 | 1700 | 150 | 3.6 | 3400 | 40.5 | 300 | 0 | - | 0
E-1 | School | ClassroomInPrimarySchool | 20 | 0.5 | 0.5 | 12.5 | 8 | 16 |  |  |  | 0 |  |  | 1568 | 1568 | 500 | 11.5 | 0 | 0 | 0 | 10 | [L/person/day] | 196
E-2 | School | ClassroomInHighSchool | 20 | 0.5 | 0.5 | 12.5 | 8 | 16 |  |  |  | 0 |  |  | 1568 | 1568 | 500 | 11.5 | 0 | 0 | 0 | 3.8 | [L/person/day] | 196
E-3 | School | StaffRoom | 20 | 0.2 | 10 | 5 | 8 | 18 |  |  | 8 | 18 |  |  | 3590 | 3590 | 500 | 10.9 | 0 | 0 | 0 | 3.8 | [L/person/day] | 359
E-4 | School | SchoolCanteen | 15 | 0.5 | 0 | 12.5 | 11 | 14 |  |  |  | 0 |  |  | 588 | 588 | 500 | 10.9 | 0 | 0 | 0 | 32 | [L/m2/day] | 196
E-5 | School | ClassroomInCollege | 20 | 0.5 | 2 | 10 | 8 | 18 |  |  |  | 0 |  |  | 1630 | 1630 | 500 | 11.5 | 0 | 0 | 0 | 3.8 | [L/person/day] | 163
E-6 | School | CollegeCanteen | 15 | 0.5 | 0 | 12.5 | 8 | 20 |  |  | 8 | 14 |  |  | 3132 | 3132 | 500 | 10.9 | 0 | 0 | 0 | 48 | [L/m2/day] | 359
E-7 | School | OfficeRoom | 20 | 0.2 | 10 | 5 | 8 | 18 |  |  |  | 0 |  |  | 2410 | 2410 | 750 | 16.3 | 0 | 0 | 0 | 3.8 | [L/person/day] | 241
E-8 | School | ResearchRoom | 20 | 0.2 | 30 | 5 | 9 | 21 |  |  | 9 | 21 |  |  | 3504 | 3504 | 750 | 16.3 | 0 | 0 | 0 | 3.8 | [L/person/day] | 292
E-9 | School | ComputerRoom | 20 | 0.5 | 60 | 12.5 | 8 | 16 |  |  |  | 0 |  |  | 1928 | 1928 | 750 | 16.6 | 0 | 0 | 0 | 3.8 | [L/person/day] | 241
E-10 | School | Laboratory | 20 | 0.5 | 60 | 12.5 | 8 | 16 |  |  |  | 0 |  |  | 1928 | 1928 | 1000 | 27.3 | 0 | 0 | 0 | 3.8 | [L/person/day] | 241
E-11 | School | PracticalRoom | 20 | 0.5 | 60 | 12.5 | 8 | 16 |  |  |  | 0 |  |  | 1928 | 1928 | 750 | 20.5 | 0 | 0 | 0 | 3.8 | [L/person/day] | 241
E-12 | School | Hall | 20 | 0.7 | 0 | 18 | 10 | 15 |  |  |  | 0 |  |  | 1205 | 723 | 500 | 14.6 | 0 | 0 | 0 | 3.8 | [L/person/day] | 241
E-13 | School | NightDutyRoom | 15 | 0.07 | 4 | 4 | 0 | 10 | 19 | 24 | 0 | 10 | 19 | 24 | 5475 | 2920 | 500 | 10.9 | 5475 | 21.6 | 300 | 165 | [L/person/day] | 365
E-14 | School | LockerRoom | 15 | 0.1 | 0 | 5 | 8 | 18 |  |  |  | 0 |  |  | 2410 | 2410 | 300 | 6.6 | 2410 | 13.5 | 300 | 62 | [L/person/day] | 241
E-15 | School | Corridor | 15 | 0.03 | 0 | 2.5 | 8 | 18 |  |  |  | 0 |  |  | 2410 | 2410 | 200 | 8 | 0 | 0 | 0 | 0 | - | 0
E-16 | School | Lobby | 35 | 0.2 | 0 | 7.5 | 8 | 18 |  |  |  | 0 |  |  | 2410 | 2410 | 300 | 12 | 0 | 0 | 0 | 3.8 | [L/person/day] | 241
E-17 | School | Toilet | 15 | 0.03 | 0 | 2.5 | 8 | 18 |  |  |  | 0 |  |  | 2410 | 2410 | 300 | 12 | 2410 | 40.5 | 300 | 0 | - | 0
E-18 | School | SmokingRoom | 15 | 0.03 | 0 | 2.5 | 8 | 18 |  |  |  | 0 |  |  | 2410 | 2410 | 300 | 6.6 | 2410 | 81 | 300 | 0 | - | 0
E-19 | School | Kitchen | [12 empty] | 0 | 1200 | 750 | 16.5 | 1200 | 135 | 600 | 0 | - | 0
E-20 | School | IndoorParking | [12 empty] | 0 | 3000 | 150 | 3.6 | 3000 | 30 | 600 | 0 | - | 0
E-21 | School | MechanicalRoom | [12 empty] | 0 | 120 | 200 | 4.9 | 8760 | 13.5 | 300 | 0 | - | 0
E-22 | School | ElectricalRoom | [12 empty] | 0 | 120 | 200 | 4.9 | 8760 | 27 | 300 | 0 | - | 0
E-23 | School | Kitchenette | [12 empty] | 0 | 600 | 300 | 6.6 | 1200 | 13.5 | 300 | 0 | - | 0
E-24 | School | StorageRoom | [12 empty] | 0 | 600 | 300 | 7.2 | 1200 | 13.5 | 300 | 0 | - | 0
E-25 | School | CopyRoom | [12 empty] | 0 | 600 | 500 | 10.9 | 1200 | 27 | 300 | 0 | - | 0
E-26 | School | GarbageStorage | [12 empty] | 0 | 600 | 150 | 3.6 | 1200 | 40.5 | 300 | 0 | - | 0
R-1 | Restaurant | Restaurant | 30 | 0.5 | 40 | 12.5 | 10 | 23 |  |  | 10 | 23 |  |  | 4745 | 4745 | 500 | 20 | 0 | 0 | 0 | 48 | [L/m2/day] | 365
R-2 | Restaurant | LightRestaurant | 20 | 0.5 | 0 | 12.5 | 10 | 23 |  |  | 10 | 23 |  |  | 4745 | 4745 | 300 | 12 | 0 | 0 | 0 | 16 | [L/m2/day] | 365
R-3 | Restaurant | CoffeeShop | 25 | 0.4 | 10 | 10 | 7 | 22 |  |  | 7 | 22 |  |  | 5475 | 5475 | 200 | 17.6 | 0 | 0 | 0 | 32 | [L/m2/day] | 365
R-4 | Restaurant | Bar | 10 | 0.2 | 0 | 5 | 18 | 24 |  |  | 18 | 24 |  |  | 1752 | 1752 | 50 | 6.8 | 0 | 0 | 0 | 32 | [L/m2/day] | 292
R-5 | Restaurant | FrontDesk | 20 | 0.1 | 0 | 2.5 | 10 | 23 |  |  | 10 | 23 |  |  | 4745 | 4745 | 500 | 11 | 0 | 0 | 0 | 0 | - | 0
R-6 | Restaurant | OfficeRoom | 15 | 0.1 | 10 | 5 | 10 | 23 |  |  | 10 | 23 |  |  | 4745 | 4745 | 750 | 16.3 | 0 | 0 | 0 | 3.8 | [L/person/day] | 365
R-7 | Restaurant | LockerRoom | 15 | 0.1 | 0 | 5 | 10 | 23 |  |  | 10 | 23 |  |  | 4745 | 4745 | 300 | 6.6 | 4745 | 13.5 | 300 | 62 | [L/person/day] | 365
R-8 | Restaurant | Corridor | 20 | 0.1 | 0 | 2.5 | 10 | 23 |  |  | 10 | 23 |  |  | 4745 | 4745 | 150 | 6 | 0 | 0 | 0 | 0 | - | 0
R-9 | Restaurant | Lobby | 20 | 0.1 | 0 | 2.5 | 10 | 23 |  |  | 10 | 23 |  |  | 4745 | 4745 | 300 | 12 | 0 | 0 | 0 | 3.8 | [L/person/day] | 365
R-10 | Restaurant | Toilet | 20 | 0.1 | 0 | 2.5 | 10 | 23 |  |  | 10 | 23 |  |  | 4745 | 4745 | 300 | 12 | 4745 | 40.5 | 300 | 0 | - | 0
R-11 | Restaurant | SmokingRoom | 20 | 0.1 | 0 | 2.5 | 10 | 23 |  |  | 10 | 23 |  |  | 4745 | 4745 | 300 | 6.6 | 4745 | 81 | 300 | 0 | - | 0
R-12 | Restaurant | Kitchen | [12 empty] | 0 | 3400 | 750 | 16.5 | 3400 | 135 | 600 | 0 | - | 0
R-13 | Restaurant | IndoorParking | [12 empty] | 0 | 5000 | 150 | 3.6 | 5000 | 30 | 600 | 0 | - | 0
R-14 | Restaurant | MechanicalRoom | [12 empty] | 0 | 340 | 200 | 4.9 | 8760 | 13.5 | 300 | 0 | - | 0
R-15 | Restaurant | ElectricalRoom | [12 empty] | 0 | 340 | 200 | 4.9 | 8760 | 27 | 300 | 0 | - | 0
R-16 | Restaurant | Kitchenette | [12 empty] | 0 | 1700 | 300 | 6.6 | 3400 | 13.5 | 300 | 0 | - | 0
R-17 | Restaurant | StorageRoom | [12 empty] | 0 | 1700 | 300 | 7.2 | 3400 | 13.5 | 300 | 0 | - | 0
R-18 | Restaurant | CopyRoom | [12 empty] | 0 | 1700 | 500 | 10.9 | 3400 | 27 | 300 | 0 | - | 0
R-19 | Restaurant | GarbageStorage | [12 empty] | 0 | 1700 | 150 | 3.6 | 3400 | 40.5 | 300 | 0 | - | 0
M-1 | MeetingPlace | GymnasiumInAthletic | 20 | 0.3 | 10 | 7.5 | 10 | 23 |  |  | 10 | 23 |  |  | 3991 | 3991 | 750 | 16.3 | 3991 | 13.5 | 300 | 62 | [L/person/day] | 307
M-2 | MeetingPlace | LobbyInAthletic | 15 | 0.1 | 0 | 2.5 | 9 | 23 |  |  | 9 | 23 |  |  | 4298 | 3991 | 500 | 10.9 | 0 | 0 | 0 | 3.8 | [L/person/day] | 307
M-3 | MeetingPlace | ToiletInAthletic | 15 | 0.1 | 0 | 2.5 | 9 | 23 |  |  | 9 | 23 |  |  | 4298 | 3991 | 300 | 12 | 3991 | 40.5 | 300 | 0 | - | 0
M-4 | MeetingPlace | SmokingRoomInAthletic | 15 | 0.1 | 0 | 2.5 | 9 | 23 |  |  | 9 | 23 |  |  | 4298 | 3991 | 300 | 6.6 | 3991 | 81 | 300 | 0 | - | 0
M-5 | MeetingPlace | SkatingRinkForOfficialCompetition | 60 | 0.1 | 0 | 12.5 | 8 | 21 |  |  | 8 | 21 |  |  | 4511 | 4164 | 1500 | 43.8 | 4164 | 13.5 | 300 | 62 | [L/person/day] | 347
M-6 | MeetingPlace | ArenaForOfficialCompetition | 60 | 0.1 | 0 | 12.5 | 8 | 21 |  |  | 8 | 21 |  |  | 4511 | 4164 | 1000 | 29.2 | 4164 | 13.5 | 300 | 62 | [L/person/day] | 347
M-7 | MeetingPlace | SkatingRinkForGeneralGame | 60 | 0.1 | 0 | 12.5 | 8 | 21 |  |  | 8 | 21 |  |  | 4511 | 4164 | 750 | 21.9 | 4164 | 13.5 | 300 | 62 | [L/person/day] | 347
M-8 | MeetingPlace | ArenaForGeneralGame | 60 | 0.1 | 0 | 12.5 | 8 | 21 |  |  | 8 | 21 |  |  | 4511 | 4164 | 500 | 14.6 | 4164 | 13.5 | 300 | 62 | [L/person/day] | 347
M-9 | MeetingPlace | SkatingRinkForRecreation | 60 | 0.1 | 0 | 12.5 | 8 | 21 |  |  | 8 | 21 |  |  | 4511 | 4164 | 300 | 8.8 | 4164 | 13.5 | 300 | 62 | [L/person/day] | 347
M-10 | MeetingPlace | ArenaForRecreation | 60 | 0.1 | 0 | 12.5 | 8 | 21 |  |  | 8 | 21 |  |  | 4511 | 4164 | 200 | 5.8 | 4164 | 13.5 | 300 | 62 | [L/person/day] | 347
M-11 | MeetingPlace | CheeringSectionInStadium | 20 | 0.4 | 0 | 10 | 8 | 21 |  |  | 8 | 21 |  |  | 4511 | 4164 | 75 | 2.3 | 0 | 0 | 0 | 3.8 | [L/person/day] | 347
M-12 | MeetingPlace | LobbyInStadium | 15 | 0.1 | 0 | 2.5 | 8 | 21 |  |  | 8 | 21 |  |  | 4511 | 4164 | 500 | 10.9 | 0 | 0 | 0 | 3.8 | [L/person/day] | 347
M-13 | MeetingPlace | ToiletInStadium | 15 | 0.1 | 0 | 2.5 | 8 | 21 |  |  | 8 | 21 |  |  | 4511 | 4164 | 300 | 12 | 4164 | 40.5 | 300 | 0 | - | 0
M-14 | MeetingPlace | SmokingRoomInStadium | 15 | 0.1 | 0 | 2.5 | 8 | 21 |  |  | 8 | 21 |  |  | 4511 | 4164 | 300 | 6.6 | 4164 | 81 | 300 | 0 | - | 0
M-15 | MeetingPlace | BathroomInBathingFacility | 10 | 0.2 | 0 | 5 | 8 | 23 |  |  | 8 | 23 |  |  | 5475 | 5110 | 300 | 13.8 | 5110 | 13.5 | 300 | 300 | [L/person/day] | 365
M-16 | MeetingPlace | LockerRoomInBathingFacility | 10 | 0.2 | 0 | 5 | 8 | 23 |  |  | 8 | 23 |  |  | 5475 | 5110 | 300 | 7.2 | 5110 | 13.5 | 300 | 300 | [L/person/day] | 365
M-17 | MeetingPlace | RestingRoomInBathingFacility | 10 | 0.2 | 0 | 5 | 8 | 23 |  |  | 8 | 23 |  |  | 5475 | 5110 | 200 | 8 | 5110 | 13.5 | 300 | 3.8 | [L/person/day] | 365
M-18 | MeetingPlace | LobbyInBathingFacility | 10 | 0.2 | 0 | 5 | 8 | 23 |  |  | 8 | 23 |  |  | 5475 | 5110 | 500 | 10.9 | 0 | 0 | 0 | 3.8 | [L/person/day] | 365
M-19 | MeetingPlace | ToiletInBathingFacility | 15 | 0.2 | 0 | 5 | 8 | 23 |  |  | 8 | 23 |  |  | 5475 | 5110 | 300 | 12 | 5110 | 40.5 | 300 | 0 | - | 0
M-20 | MeetingPlace | SmokingRoomInBathingFacility | 15 | 0.2 | 0 | 5 | 8 | 23 |  |  | 8 | 23 |  |  | 5475 | 5110 | 300 | 6.6 | 5110 | 81 | 300 | 0 | - | 0
M-21 | MeetingPlace | AuditoriumInMovieTheater | 15 | 1 | 0 | 25 | 8 | 24 |  |  | 8 | 24 |  |  | 5840 | 1095 | 300 | 12 | 0 | 0 | 0 | 3.8 | [L/person/day] | 365
M-22 | MeetingPlace | LobbyInMovieTheater | 15 | 0.1 | 0 | 2.5 | 8 | 24 |  |  | 8 | 24 |  |  | 5840 | 5475 | 300 | 12 | 0 | 0 | 0 | 3.8 | [L/person/day] | 365
M-23 | MeetingPlace | ToiletInMovieTheater | 15 | 0.2 | 0 | 5 | 8 | 24 |  |  | 8 | 24 |  |  | 5840 | 5475 | 300 | 12 | 5475 | 40.5 | 300 | 0 | - | 0
M-24 | MeetingPlace | SmokingRoomInMovieTheater | 15 | 0.2 | 0 | 5 | 8 | 24 |  |  | 8 | 24 |  |  | 5840 | 5475 | 300 | 6.6 | 5475 | 81 | 300 | 0 | - | 0
M-25 | MeetingPlace | Library | 15 | 0.2 | 3 | 7 | 8 | 19 |  |  | 8 | 19 |  |  | 3377 | 3070 | 750 | 16.3 | 0 | 0 | 0 | 3.8 | [L/person/day] | 307
M-26 | MeetingPlace | LobbyInLibrary | 15 | 0.2 | 0 | 5 | 8 | 19 |  |  | 8 | 19 |  |  | 3377 | 3070 | 300 | 12 | 0 | 0 | 0 | 3.8 | [L/person/day] | 307
M-27 | MeetingPlace | ToiletInLibrary | 15 | 0.2 | 0 | 5 | 8 | 19 |  |  | 8 | 19 |  |  | 3377 | 3070 | 300 | 12 | 3070 | 40.5 | 300 | 0 | - | 0
M-28 | MeetingPlace | SmokingRoomInLibrary | 15 | 0.2 | 0 | 5 | 8 | 19 |  |  | 8 | 19 |  |  | 3377 | 3070 | 300 | 6.6 | 3070 | 81 | 300 | 0 | - | 0
M-29 | MeetingPlace | Museum | 15 | 0.03 | 0 | 6 | 8 | 17 |  |  | 8 | 17 |  |  | 2763 | 2456 | 500 | 10.9 | 0 | 0 | 0 | 3.8 | [L/person/day] | 307
M-30 | MeetingPlace | LobbyInMuseum | 15 | 0.2 | 0 | 5 | 8 | 17 |  |  | 8 | 17 |  |  | 2763 | 2456 | 300 | 12 | 0 | 0 | 0 | 3.8 | [L/person/day] | 307
M-31 | MeetingPlace | ToiletInMuseum | 15 | 0.2 | 0 | 5 | 8 | 17 |  |  | 8 | 17 |  |  | 2763 | 2456 | 300 | 12 | 2456 | 40.5 | 300 | 0 | - | 0
M-32 | MeetingPlace | SmokingRoomInMuseum | 15 | 0.2 | 0 | 5 | 8 | 17 |  |  | 8 | 17 |  |  | 2763 | 2456 | 300 | 6.6 | 2456 | 81 | 300 | 0 | - | 0
M-33 | MeetingPlace | DressingRoom | 25 | 0.2 | 0 | 5 | 9 | 20 |  |  | 9 | 20 |  |  | 2761 | 2510 | 500 | 12.2 | 0 | 0 | 0 | 3.8 | [L/person/day] | 251
M-34 | MeetingPlace | BoardInTheater | 50 | 1 | 0 | 25 | 10 | 20 |  |  | 10 | 20 |  |  | 2510 | 2259 | 500 | 20 | 0 | 0 | 0 | 3.8 | [L/person/day] | 251
M-35 | MeetingPlace | AudienceSeatInTheater | 50 | 1 | 0 | 25 | 10 | 20 |  |  | 10 | 20 |  |  | 2510 | 2259 | 300 | 12 | 0 | 0 | 0 | 3.8 | [L/person/day] | 251
M-36 | MeetingPlace | LobbyInTheater | 15 | 0.2 | 0 | 5 | 10 | 20 |  |  | 10 | 20 |  |  | 2510 | 2259 | 300 | 12 | 0 | 0 | 0 | 3.8 | [L/person/day] | 251
M-37 | MeetingPlace | ToiletInTheater | 15 | 0.2 | 0 | 5 | 10 | 20 |  |  | 10 | 20 |  |  | 2510 | 2259 | 300 | 12 | 2259 | 40.5 | 300 | 0 | - | 0
M-38 | MeetingPlace | SmokingRoomInTheater | 15 | 0.2 | 0 | 5 | 10 | 20 |  |  | 10 | 20 |  |  | 2510 | 2259 | 300 | 6.6 | 2259 | 81 | 300 | 0 | - | 0
M-39 | MeetingPlace | Karaoke | 15 | 0.4 | 5 | 10 | 0 | 24 |  |  | 0 | 24 |  |  | 8760 | 8760 | 400 | 16 | 8760 | 40.5 | 300 | 3.8 | [L/person/day] | 365
M-41 | MeetingPlace | Bowlling | 15 | 0.1 | 15 | 2.5 | 9 | 24 |  |  | 9 | 24 |  |  | 5475 | 5110 | 400 | 16 | 5110 | 40.5 | 300 | 3.8 | [L/person/day] | 365
M-42 | MeetingPlace | Pachinko | 60 | 0.5 | 100 | 25 | 9 | 23 |  |  | 9 | 23 |  |  | 5110 | 4745 | 1000 | 22 | 4745 | 40.5 | 300 | 3.8 | [L/person/day] | 365
M-43 | MeetingPlace | AuditoriumInRaceCourse | 20 | 0.4 | 12 | 10 | 9 | 18 |  |  | 9 | 18 |  |  | 3123 | 2776 | 500 | 11 | 0 | 0 | 0 | 3.8 | [L/person/day] | 347
M-44 | MeetingPlace | TicketOfficeInRaceCourse | 15 | 0.1 | 0 | 2.5 | 9 | 18 |  |  | 9 | 18 |  |  | 3123 | 2776 | 500 | 11 | 0 | 0 | 0 | 0 | - | 0
M-45 | MeetingPlace | ShopInRaceCourse | 15 | 0.1 | 0 | 2.5 | 9 | 18 |  |  | 9 | 18 |  |  | 3123 | 2776 | 500 | 11 | 0 | 0 | 0 | 0 | - | 0
M-46 | MeetingPlace | LobbyInRaceCourse | 15 | 0.1 | 0 | 2.5 | 9 | 18 |  |  | 9 | 18 |  |  | 3123 | 2776 | 300 | 12 | 0 | 0 | 0 | 3.8 | [L/person/day] | 347
M-47 | MeetingPlace | ToiletInRaceCourse | 15 | 0.1 | 0 | 2.5 | 9 | 18 |  |  | 9 | 18 |  |  | 3123 | 2776 | 300 | 12 | 3123 | 40.5 | 300 | 0 | - | 0
M-48 | MeetingPlace | SmokingRoomInRaceCourse | 15 | 0.1 | 0 | 2.5 | 9 | 18 |  |  | 9 | 18 |  |  | 3123 | 2776 | 300 | 6.6 | 3123 | 81 | 300 | 0 | - | 0
M-49 | MeetingPlace | MainHallInTemple | 10 | 1 | 0 | 25 | 7 | 18 |  |  | 7 | 18 |  |  | 2761 | 2510 | 300 | 8.1 | 0 | 0 | 0 | 3.8 | [L/person/day] | 251
M-50 | MeetingPlace | LobbyInTemple | 15 | 0.2 | 0 | 5 | 7 | 18 |  |  | 7 | 18 |  |  | 2761 | 2510 | 300 | 12 | 0 | 0 | 0 | 3.8 | [L/person/day] | 251
M-51 | MeetingPlace | ToiletInTemple | 15 | 0.2 | 0 | 5 | 7 | 18 |  |  | 7 | 18 |  |  | 2761 | 2510 | 300 | 12 | 2510 | 40.5 | 300 | 0 | - | 0
M-52 | MeetingPlace | SmokingRoomInTemple | 15 | 0.2 | 0 | 5 | 7 | 18 |  |  | 7 | 18 |  |  | 2761 | 2510 | 300 | 6.6 | 2510 | 81 | 300 | 0 | - | 0
M-53 | MeetingPlace | Kitchen | [12 empty] | 0 | 4000 | 750 | 16.5 | 4000 | 135 | 600 | 0 | - | 0
M-54 | MeetingPlace | IndoorParking | [12 empty] | 0 | 4000 | 150 | 3.6 | 4000 | 30 | 600 | 0 | - | 0
M-55 | MeetingPlace | MechanicalRoom | [12 empty] | 0 | 400 | 200 | 4.9 | 8760 | 13.5 | 300 | 0 | - | 0
M-56 | MeetingPlace | ElectricalRoom | [12 empty] | 0 | 400 | 200 | 4.9 | 8760 | 27 | 300 | 0 | - | 0
M-57 | MeetingPlace | Kitchenette | [12 empty] | 0 | 2000 | 300 | 6.6 | 4000 | 13.5 | 300 | 0 | - | 0
M-58 | MeetingPlace | StorageRoom | [12 empty] | 0 | 2000 | 300 | 7.2 | 4000 | 13.5 | 300 | 0 | - | 0
M-59 | MeetingPlace | CopyRoom | [12 empty] | 0 | 2000 | 500 | 10.9 | 4000 | 27 | 300 | 0 | - | 0
M-60 | MeetingPlace | GarbageStorage | [12 empty] | 0 | 2000 | 150 | 3.6 | 4000 | 40.5 | 300 | 0 | - | 0
F-1 | Factory | WareHouse | [12 empty] | 0 | 3000 | 300 | 7.2 | 0 | 0 | 0 | 0 | - | 0
F-2 | Factory | OutdoorParikng | [12 empty] | 0 | 3000 | 150 | 3.6 | 0 | 0 | 0 | 0 | - | 0
A-1 | ApartmentHouse | IndoorCorridor | 10 | 0 | 0 | 2.5 | 0 | 24 |  |  | 0 | 24 |  |  | 8760 | 8760 | 150 | 6 | 0 | 0 | 0 | 0 | [L/person/day] | 0
A-2 | ApartmentHouse | Lobby | 20 | 0 | 0 | 2.5 | 0 | 24 |  |  | 0 | 24 |  |  | 8760 | 8760 | 300 | 12 | 0 | 0 | 0 | 0 | [L/person/day] | 0
A-3 | ApartmentHouse | ManagerRoom | 12 | 0.1 | 12 | 5 | 8 | 17 |  |  | 9 | 12 |  |  | 2322 | 2322 | 750 | 16.3 | 0 | 0 | 0 | 3.8 | [L/person/day] | 292
A-4 | ApartmentHouse | AssemblyRoom | 10 | 0.25 | 2 | 12 | 10 | 16 |  |  | 11 | 14 |  |  | 1599 | 1066 | 500 | 10.9 | 0 | 0 | 0 | 1.5 | [L/m2/day] | 292
A-5 | ApartmentHouse | OutdoorCorridor | [12 empty] | 0 | 4380 | 75 | 6 | 0 | 0 | 0 | 0 | - | 0
A-6 | ApartmentHouse | IndoorParking | [12 empty] | 0 | 8760 | 150 | 3.6 | 5110 | 30 | 300 | 0 | - | 0
A-7 | ApartmentHouse | MechanicalRoom | [12 empty] | 0 | 200 | 200 | 4.9 | 8760 | 12.5 | 300 | 0 | - | 0
A-8 | ApartmentHouse | ElectricalRoom | [12 empty] | 0 | 200 | 200 | 4.9 | 8760 | 25 | 300 | 0 | - | 0
A-9 | ApartmentHouse | GarbageStorage | [12 empty] | 0 | 8760 | 150 | 3.6 | 8760 | 37.5 | 300 | 0 | - | 0
C-1 | Common | NonACRoom | 3 | 0 | 3 | 0 | 0 | 24 |  |  | 0 | 24 |  |  | 8760 | 0 |  |  | 0 |  |  |  |  | 0